Smoke Detector (SD-16ZW)
The SD-16ZW Smoke Detector is a wirelessly operated photo-electronic smoke detector designed to operate with any Z-Wave enabled controller devices. The Smoke Detector’s alarm situations, battery condition, operating conditions, supervisory data and general fault information are sent to the Z-Wave Gateway/Control Panel wirelessly.
The Smoke Detector is a Z-Wave enabled device and is fully compatible with any Z-Wave enabled network.
Z-Wave is a wireless communication protocol that uses a low-power RF radio. By taking advantage of the Z-Wave mesh network, commands can be transmitted to their destination via intermediary “listening” Z-Wave products.
The Smoke Detector calibrates for the air contents after warming up to determine a standard condition for the environment. It can also be manually instructed to calibrate for air content. It is also pre-programmed to automatically calibrate once a month.

Mounting the Smoke Detector is simplified with the mounting bracket, where the mounting bracket is fixed to the surface using screws and dowels. The Smoke Detector is then fixed to the mounting bracket by hooking itself onto the mounting bracket.
· Identifying the Parts
[image: image9.wmf]
1. Red LED

When the Smoke Detector is triggered, the Red LED will flash quickly for 10 seconds. The Smoke Detector will continuously check for smoke condition every 10 seconds and flash quickly for 10 seconds again if the condition persists.
While the Smoke Detector is transmitting a signal, the Red LED will turn on.
After the battery is inserted and the Smoke Detector is in warming and calibration process, the Red LED will flash once every 2 seconds for 2-8 min.

The Red LED will flash once every 4 seconds along with the Yellow LED when the battery cannot supply enough power for normal operation.
2. Yellow LED

When the battery voltage is low, the Yellow LED will flash once every 45 seconds.

When auto calibration (1 calibration per month) fails, the yellow LED will flash once every 1 second.

The Yellow LED will flash once every 4 seconds along with the Red LED when the battery cannot supply enough power for normal operation.

3. Function Button

· Pressing the Function Button 3 times within 1.5 seconds to send a learn code.
· Pressing the Function Button for 10 seconds to factory reset.
· Transmit a radio signal for testing the radio communication range.

· Test if the Smoke Detector is functioning normally.

· Silence the Smoke Detector’s alarm
4. Buzzer

When the Smoke Detector is triggered, the buzzer will start a local alarm of 85dB (in compliance with the UL Standard). One local alarm cycle is of the pattern:

0.5 second beep, 0.5 second silence, 0.5 second beep, 0.5 second silence, 0.5 second beep, 1.5 second silence. The cycle is repeated continuously.

If the battery voltage is low, the buzzer will emit a low-volume beep to accompany the Yellow LED flash every 45 seconds.

5. Mounting Hole

The Hook of the Mounting Bracket can hook into this Mounting Hole

6. Battery compartment
To fit in two AA 1.5V Alkaline Batteries.
7. Battery Compartment Cover

8. Mounting Bracket
9. Hook
· Battery

· Two AA 1.5V Alkaline Batteries are used to supply power to the Smoke Detector. 
· The Smoke Detector will report its battery percentage to the Control Panel respectively at 100%, 75%, 50%, 25%. If the battery voltage is low (25%), a Low Battery signal will be sent to the Control Panel to notify the user.
· When the Smoke Detector is low on battery, a low battery signal will be transmitted along with regular signal transmissions. If the battery voltage is low, the Yellow LED will flash with accompanying low-volume beep once every 45 seconds and inform the Z-Wave Gateway/Control Panel regularly.
· The Red and Yellow LED will flash once every 4 seconds when the battery cannot supply enough power for normal operation.

<NOTE>

· When changing batteries, after removing the old batteries, press the Function button twice to fully discharge before inserting new batteries.
· Installation Procedures

Step 1.
Insert the two AA 1.5V Alkaline Batteries into the battery compartment. Orient the battery according to the battery compartment polarity indication before insertion.

Step 2.
After the battery is inserted, the Smoke Detector will sound 2 short beeps, Red LED will start to flash and initiates a 1-minute warm-up period.

Step 3.
During the 1-minute warming period, you can learn (include) the Smoke Detector into the Panel, refer to Adding Device (Inclusion) for details.
Step 4.

When the 1-minute warming period is over, one short beep will sound to indicate that the Smoke Detector is starting calibration process. The process will be repeated every 40 seconds and notified by a short beep respectively. The completion of calibration process will be notified by a 2-tone beep and the Red LED will turn off.

Normally it takes about 7 minutes to do the calibration (a maximum of 8 calibration attempts). However, after 7 minutes, if the Smoke Detector gives out continuous beeps instead, it indicates that the Smoke Detector has failed the calibration. Remove the battery to silence the beeps. Start from step 1 to try again after a pause of at least 30 seconds.
<NOTE>

· During the calibration period, pressing the Function Button is prohibited. If you are not able to do the learning process (Step 3) during the 1-minute warming period, please do the learning process after the calibration period (Step 4).
· [image: image1.jpg]


A strong transmission path between the Z-Wave Gateway/Control Panel and the Smoke Detector is mandatory at the desired mounting location.

Step 5.
After the warming-up and calibration process, if the Smoke Detector is not learned (included) into the Z-Wave gateway/Control Panel, learn the Smoke Detector into the system again.

Step 6.
To check if there is a strong transmission path between the Z-Wave Gateway/Control Panel and the Smoke Detector after learnt-in, put the Z-Wave Gateway/Control Panel into “Walk Test” mode. Decide upon a suitable mounting location and press the Function button to confirm the transmission strength (Please refer to the Z-Wave Gateway/Control Panel user manual on how to determine the transmission strength).
Step 7.
Using the bracket as a template, drill two holes in the exact location, the device is to be mounted and insert the dowels.

Step 8.
Screw the bracket on by screwing the screws into the dowels. The two hooks will need to be facing away from the surface.
Step 9.
Locate the single line mark on the detector and line it up with one of the hook of the bracket. After both hooks fits in the two mounting holes on the detector, rotate the detector as shown in the picture on the right to lock it in onto the bracket. The installation is now complete.
· Testing the Smoke Detector

By pressing the Function button on the Smoke Detector, you can test if the Smoke Detector is functioning normally.

· If the Smoke Detector functions normally, the Red LED will be on for 2 seconds followed by a 2-tone beep.

· If the buzzer sounds 2-tone beeps 3 times, the “Optical Chamber” on the Smoke Detector is either dirty or out-of-order.

· If the Red LED doesn’t light and no beep is sounded, it means the Smoke Detector is out-of-order. 

· Supervisory Signal

· This function uses the Z-Wave Wake Up Command Class. The Wake Up Command Class allows the battery-powered Smoke Detector to notify the Control Panel/Gateway that it is awake and ready to receive any queued commands. The wake up time is programmed automatically according to Control Panel’s setting when The Smoke Detector is included. The recommended setting of the wake up time is 60 minutes above.
· Alarm Silence

· Once the alarm is sounding, pressing the Function button will put the Smoke Detector into Alarm Silence mode for 10 minutes and the alarm will be stopped.

· During this 10-minute Alarm Silence period, the Red LED will flash once per second. 

· After this 10-minute period is over, the Smoke Detector will sound a 2-tone beep, send an alarm restore signal to the Z-Wave Gateway/Control Panel and returns to normal operation mode. If the Smoke concentration is still over the set threshold value, the Smoke Detector will sound the alarm again.

· Recalibration
As the operation condition of the smoke detector may vary after being installed for some time, you may wish to recalibrate the smoke detector to take a new smoke detection threshold value and ensure optimal performance of the smoke detector. To do this, 

· Press 10 seconds on the Function button and hold until the Red LED starts to flash. The Smoke Detector will sound 2 short beeps then follow the calibration process described in step 4 of Installation Procedure to take the new reference value.

· Every time the battery is removed and reinserted, the Smoke Detector will also take the new threshold value following the warming and calibration process.

· Auto-Calibration

· After first installation, Smoke Detector will perform auto-calibration after 4 hours. Afterwards it will perform auto-calibration once every month. During the auto-calibration process, Smoke Detector will not emit any sound. Each calibration sampling process takes 40 seconds. If the process fails, it will retry. The Smoke Detector will sample for a maximum of 5 times (including the initial auto-calibration). If the last retry fails, the Yellow LED will start to flash once every 1 second and the Smoke Detector will send calibration failure code to the Z-Wave Gateway/control panel. The Yellow LED flashing can be cancelled by removing and reloading the battery, or by manually starting the calibration process. However if the manual calibration fails again, Smoke Detector will emit continuous beeps and the Red LED will also flash continuously. In this case you need to remove and reload the battery to stop the beeping sound (please wait for 30 seconds after removing batteries before reloading them.)

<NOTE>

· When Smoke Detector auto calibration fails, the smoke alarm function will still work normally using the threshold value taken from last successful calibration
· Detecting the Smoke 

· Once the concentration of the smoke exceeds the set threshold value, the Smoke Detector lights up its Red LED to indicate it is sending the Smoke Alarm signal to the Z-Wave Gateway/Control Panel. After the transmission is completed, the Smoke Detector then activates its buzzer with the Red LED flashing rapidly for 10 seconds for local warning.

· After this 10-second local warning period, the Smoke Detector proceeds to perform a follow-up smoke check.  If the smoke concentration is found to be alarming still, the Smoke Detector will repeat another 10 seconds of local warning with buzzer and rapid flashing Red LED.

· The Smoke Detector will repeatedly perform follow-up checks until the smoke concentration is lower than the set value, then the alarm will be stopped automatically or the alarm can be stopped manually by using the “Alarm Silence” function.

· Once a Smoke Alarm Signal has been transmitted, the Smoke Detector will continue to send alarm signals every 2 minutes when the smoke concentration continues to be higher than allowed. This 2-minute cycle will be repeated until the smoke concentration is lower than the set value, then the alarm will be stopped automatically or the alarm can be stopped manually by using the “Alarm Silence” function.
· Adding Device (Inclusion)
This product can be included and operated in any Z-Wave network with other Z-Wave certified devices from other manufactures and/or other applications. All non-battery operated nodes within the network will act as repeaters regardless of vendor to increase reliability of the network.

· Put the Z-Wave gateway or control panel into Inclusion or Learning mode (please refer to the Z-Wave gateway or control panel manual).

· Within 1.5 seconds, press the Function button 3 times. The Smoke Detector will emit a 2-tone beep and the LED will turn on for ~2 seconds.

· Refer to the operation manual of the Z-Wave gateway or control panel to complete the learn-in process.
· If the sensor has already been included (learnt) into another Z-Wave Gateway/Control Panel, or if the sensor is unable to be learnt into the current Z-Wave Gateway/Control Panel, please exclude it first (see Exclusion) before attempting to include it into the current Z-Wave Gateway/Control Panel.

· When the 1-minute warming period is over, the Smoke Detector will start calibration process. 
· Removing Device (Exclusion)
The Smoke Detector must be removed from existing Z-Wave network before being included into another. There are two methods available to exclude a device.

Exclusion Mode

· Put the Z-Wave gateway or control panel into Exclusion mode (please refer to the Z-Wave gateway or control panel manual).

· Within 1.5 seconds, press the Function button 3 times and the Smoke Detector will be removed from the Z-Wave network.

Factory Reset

(Only use factory reset when network Control Panel/Gateway is missing or inoperable).
· Press and hold the Function button of the Smoke Detector for 10 seconds to factory reset.

<NOTE>

· Factory resetting the Smoke Detector will restore it to factory default settings (excluded from the Z-Wave network). The Z-Wave gateway or control panel will still keep its Z-Wave settings. Please refer to the gateway or control panel manual on how to remove the Smoke Detector’s Z-Wave settings.

· Range Test


To test whether the device is able to communicate with the Z-Wave gateway or control panel:

· Put the gateway / panel into range test mode (Walk Test).

· Press the Function button on the device

· The gateway / panel should display if the device is within the operation range (please refer to the operation manual of the gateway / panel).
· Z-Wave Sleep Mode

· The Smoke Detector will enter Z-Wave Sleep mode (to conserve power) after waking up for a short period of time (~10 seconds). While in Z-Wave sleep mode, Z-Wave gateways or control panels are unable to send commands to the Smoke Detector.

· To program the Smoke Detector, please send command(s) to the Smoke Detector within the wake-up period.
· [image: image7.jpg]


Installation Note

· It is recommended that the installation site be in the center area of the ceiling.

· Do not locate the detector in the following locations:

· The Kitchen – Smoke from cooking might cause an unwanted alarm.

· Near a ventilating fan, florescent lamp or air-conditioning equipment – air drafts from them may affect the sensitivity of the detector.

· [image: image8.wmf]Near ceiling beams or over a cabinet – stagnant air in these areas may affect the sensitivity of the detector.

· In the peak of an “A” frame type of ceiling. 
· Maintenance

The top cover and the smoke detecting chamber can be detached from the Smoke Detector for maintenance. Follow the steps below to maintain the smoke detecting chamber:

Step 1.
Remove the top cover by rotating the top cover counter-clockwise:

[image: image2.jpg]


        [image: image3.jpg]



Step 2.
Pull out the smoke detecting chamber:
[image: image4.jpg]



Step 3.
Pull out the anti-insect mesh inside the chamber and clean the chamber and mesh with a brush or water.

Step 4.
Re-insert the anti-insect mesh into the chamber and insert the chamber back onto the Smoke Detector. Please make sure the chamber is dry before re-inserting back onto the Smoke Detector.

[image: image5.jpg]



Step 5.
Insert the top cover back onto the Smoke Detector. The top cover includes 3 insertion hooks to stabilize. Each hook has a number next to it. Match these numbers with the numbers on the Smoke Detector.
[image: image6.jpg]Insertion Hole 1 Insertion Hole 2

Insertion Hole 3




· Z-Wave Information

Device Type: Sensor - Notification

Role Type: Reporting Sleeping Slave (RSS)

Command Class Support/Control

Mandatory CC Support:
Association CC, v2 or newer







Association Group Information CC







Battery CC







Device Reset Locally CC







Manufacturer Specific CC







Notification CC






Powerlevel CC







Version CC, v2 or newer







Wake UP CC







Z-Wave Plus Info CC

· Z-Wave’s Groups (Association Command Class Version 2)

The Smoke Detector can be set to send reports to associated Z-Wave devices. It supports 3 association groups with five nodes each. 

Group 1 for “LifeLine”:

Notification CC,V4 (COMMAND_CLASS_NOTIFICATION)



Battery CC (COMMAND_CLASS_BASIC)




Device Reset Locally CC



(it supports 1 node)
Group 2 for “Basic Set”:




Basic CC, v2 (COMMAND_CLASS_BASIC)



(it supports 5 nodes)
Group 3 for “Notification Report”:

Notification CC,V4 (COMMAND_CLASS_NOTIFICATION)
(it supports 5 nodes)

· Trigger Report (smoke detected)
When the Smoke Detector is triggered, it will transmit Notification command (Notification Type:0x01, Event:0x02) to all nodes in Group1 and 3, and Basic set (0xFF) commands to the nodes in Group 2.

· Restore Report (smoke dissipate)

When the surrounding smoke has dissipated, it will transmit Notification command (Notification Type:0x01, Event:0x00 with one parameter 0x02) to all nodes in Group 1 and 3, and Basic set (0x00) commands to the nodes in Group 2. 
· Low Battery Report
1. When low battery voltage is detected, the Smoke Detector will transmit Battery command to all nodes in Group 1.
2. When the Smoke Detector on low battery has its battery replaced, it will transmit Battery restore command to all nodes in Group 1
· Factory Reset
When the Smoke Detector is reset to factory default, it will send Device Reset Locally to all nodes in Group 1.
PAGE  

