Heat Detector (HD-9ZW) 
HD-9 is a heat detector with both rate-of-rise and fixed temperature sensors insides. It provides capacities of monitoring the rate of any rise in temperature and detecting a household temperature that may lead to a fire disaster. It is ideal for applications for the environment affected by heat, such as kitchen.

The Heat Detector is a Z-Wave enabled device and is fully compatible with any Z-Wave enabled network.

Z-Wave is a wireless communication protocol that uses a low-power RF radio. By taking advantage of the Z-Wave mesh network, commands can be transmitted to their destination via intermediary “listening” Z-Wave products.

HD-9 is designed to detect two temperature conditions. It signals an alarm if temperature increases by 8.3 °C per minute. The alarm is also activated if the temperature exceeds the threshold temperature of 57.3°C. The intelligent design allows appropriate action to be taken and eliminates fire hazards.
[image: image3.jpg]Mounting holes for
the bracket

=Y




1. Red LED

· When HD-9 is reporting an alarm, the LED will turn on for 1.5 seconds, and afterwards, the LED will flash until the temperature is restored.
· When the Heat Detector has low battery, the LED will flash once every 30 seconds (HD-9 will also emit a beep)
· When the temperature sensor of HD-9 is out-of-order, the LED will flash once every 60 seconds (HD-9 will also emit a beep)

· During Alarm Silence period, the LED will flash once per second.

2.Test Button

· Press 3 times within 1.5 seconds to transmit a learn code and HD-9 will emit a 2-tone beep
· Press once to test if the Heat Detector is functioning normally
· Press once to silence the alarm

3. Battery compartment
4. Mounting Hole

5. Mounting Bracket

· Battery

· 3 “AA” Alkaline batteries are used to supply power.
· The Heat Detector will report its battery percentage to the Control Panel respectively at 100%, 75%, 50% and 25%. If the battery voltage is low (25%), a Low Battery signal will be sent to the Control Panel to notify the user.
· When the Heat Detector is under low battery condition, a low battery signal will be transmitted along with regular signal transmissions. If the battery voltage is low, HD-9 will emit one beep and the LED will flash once every 30 seconds and inform the Control Panel regularly.
<NOTE>
· When changing batteries, after removing the old batteries, press the Test button twice to fully discharge before inserting new batteries.
· Adding Device (Inclusion)

This product can be included and operated in any Z-Wave network with other Z-Wave certified devices from other manufactures and/or other applications. All non-battery operated nodes within the network will act as repeaters regardless of vendor to increase reliability of the network.
· Insert the 3 “AA” batteries into the battery compartment connecting the correct polarity as shown on the battery compartment lid.
· HD-9 will emit a 2-tone beep.

· Put the Z-Wave gateway or control panel into Inclusion or Learning mode (please refer to the Z-Wave gateway or control panel manual).

· Within 1.5 seconds, press the Test Button 3 times. HD-9 will emit a 2-tone beep.
· Refer to the operation manual of the Z-Wave gateway or control panel to complete the learn-in process.
· If the sensor has already been included (learnt) into another Z-Wave Gateway/Control Panel, or if the sensor is unable to be learnt into the current Z-Wave Gateway/Control Panel, please exclude it first (see Exclusion) before attempting to include it into the current Z-Wave Gateway/Control Panel.
· Removing Device (Exclusion)
The Heat Detector must be removed from existing Z-Wave network before being included into another. There are two methods available to exclude a device.

Exclusion Mode

· Put the Z-Wave gateway or control panel into Exclusion mode (please refer to the Z-Wave gateway or control panel manual).

· Within 1.5 seconds, press the Test Button 3 times and the Heat Detector will be removed from the Z-Wave network.

Factory Reset
(Only use factory reset when network Control Panel/Gateway is missing or inoperable).
· Remove the batteries of the Heat Detector first.
· Press and hold the Test Button. While holding the Test Button, power on the Heat Detector by re-inserting the batteries, wait for 10 seconds to factory reset.

<NOTE>

· Factory resetting the Heat Detector will restore it to factory default settings (excluded from the Z-Wave network). The Z-Wave gateway or control panel will still keep its Z-Wave settings. Please refer to the gateway or control panel manual on how to remove the Heat Detector’s Z-Wave settings.
· Range Test


To test whether the device is able to communicate with the Z-Wave gateway or control panel:

· Put the gateway / panel into range test mode (Walk Test).

· Press the Test Button on the device

· The gateway / panel should display if the device is within the operation range (please refer to the operation manual of the gateway / panel).

· Z-Wave Sleep Mode

· The Heat Detector will enter Z-Wave Sleep mode (to conserve power) after waking up for a short period of time (~10 seconds). While in Z-Wave sleep mode, Z-Wave gateways or control panels are unable to send commands to the Heat Detector.
· To program the Heat Detector, please send command(s) to the Heat Detector within the wake-up period.

· [image: image1.jpg]


Mounting
· Using the bracket as a template, mark the two holes according to the picture on the right to stabilize the bracket onto the surface.
· Insert the dowels.

· Screw the screws into the dowels to stabilize the bracket. The two hooks should be facing you.
· Locate the single line mark on the detector and line it up with one of the hooks of the bracket. After both hooks fits in the two mounting holes on the detector, rotate the detector clockwise to lock onto the bracket.
[image: image2.jpg]



· Testing the Heat Detector

By pressing the Test button on the Heat Detector, you can test if the Heat Detector is functioning normally.

· If the Heat Detector functions normally, the LED will turn on for 1 second followed by emitting a 2-tone beep.

· If the “Temperature Sensor” of the Heat Detector is out-of-order, the buzzer will emit the 2-tone beep for 3 times.
· The Heat Detector is out-of-order if nothing happens (buzzer or LED).
· Supervisory Signal

This function uses the Z-Wave Wake Up Command Class. The Wake Up Command Class allows the battery-powered Heat Detector to notify the Control Panel/Gateway that it is awake and ready to receive any queued commands. The wake up time is programmed automatically according to Control Panel’s setting when The Heat Detector is included. The recommended setting of the wake up time is 60 minutes above.
· Temperature Detection
· Once the temperature rises by 8.3 °C per minute (rise rate) or exceeds the threshold temperature of 57.3 °C, the Heat Detector lights up its LED to indicate it is sending an alarm report. HD-9 then activates its buzzer with LED flashing rapidly for 10 seconds for local warning.
· After this 10-second local warning period, HD-9 performs a follow-up temperature check. If the temperature is found to be alarming still, HD-9 will repeat another 10 seconds of local warning with buzzer and rapid flashing LED. 
· HD-9 will repeatedly perform follow-up checks until the temperature is lower than the set value of 49°C or the temperature falls by 4°C. The alarm will stop automatically if the temperature drops below 49°C or falls by 4°C (for alarms triggered by temperature rise rate, the alarm will only stop if the temperature also drops lower than 49°C). The alarm can also be stopped manually by using the “Alarm Silence” function.
· Alarm Silence

· Once the alarm is started, pressing the Test button will put the Heat Detector into Alarm Silence mode for 10 minutes and the alarm will be stopped.

· During this 10-minute Alarm Silence period, the LED will flash once per second.
· After this 10-minute period is over, the Heat Detector will emit 2 beeps and then returns to normal operation mode. If the temperature is still over the set threshold value, the Heat Detector will start alarming again.
· Installation Note

· It is recommended to install HD-9 at the center area of the ceiling.

· Do not locate the detector in the following locations:

· Close to a cooker, stove or oven  
· High humidity area, such as location near dishwasher or washing machine. 
· In front of air supply pile used for heating and air conditioning. 
· Near ceiling fan or other high air flow area  

· Z-Wave Information

Device Type: Sensor - Notification

Role Type: Reporting Sleeping Slave (RSS)

Command Class Support/Control

Mandatory CC Support:
Association CC, v2 or newer







Association Group Information CC







Battery CC







Device Reset Locally CC







Manufacturer Specific CC







Notification CC







Powerlevel CC







Version CC, v2 or newer







Wake UP CC







Z-Wave Plus Info CC

· Z-Wave’s Groups (Association Command Class Version 2)

The Heat Detector can be set to send reports to associated Z-Wave devices. It supports 3 association groups with five nodes each. 

Group 1 for “LifeLine”:

Notification CC,V4 (COMMAND_CLASS_NOTIFICATION)




Battery CC (COMMAND_CLASS_BASIC)




Device Reset Locally CC
Group 2 for “Basic Set”:




Basic CC, v2 (COMMAND_CLASS_BASIC)

Group 3 for “Notification Report”:

Notification CC,V4 (COMMAND_CLASS_NOTIFICATION)

· Trigger Report (high temperature detected)
When the Heat Detector is triggered, it will transmit Notification command (Notification Type:0x04, Event:0x02) to all nodes in Group1 and 3, and Basic set (0xFF) commands to the nodes in Group 2.

· Restore Report (High temperature calmed)

When high temperature cool down, it will transmit Notification command (Notification Type:0x04, Event:0x06) to all nodes in Group 1 and 3, and Basic set (0x00) commands to the nodes in Group 2. 
· Low Battery Report
1. When low battery voltage is detected, the Smoke Detector will transmit Battery command to all nodes in Group 1.
2. When the Smoke Detector on low battery has its battery replaced, it will transmit Battery restore command to all nodes in Group 1.
· Factory Reset
When the Smoke Detector is reset to factory default, it will send Device Reset Locally to all nodes in Group 1.
PAGE  
4

