Addendum to T6 Pro Z-Wave Programmable Thermostat Professional Install Guide

Z-Wave configuration parameters for TH6320ZW2007 If your gateway/hub/controller supports configuration function, you may remotely configure or change the default thermostat configuration parameters. See the chart below.

| Parameter Number | Name | Descript. | Format | Size | Min Value | Max Value | Default Value | Flag Advanced |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Schedule Type | 0 = Occupancy; 1 = Every day the same; 2 = 5-2 Schedule; 3 = 5-1-1 Schedule; 4 = Every day individual | 2 | 1 | 0 | 4 | 0x02 |  |
| 10 | EM Heat Type | 0 = Electric; 1 = Gas/Oil | 2 | 1 | 0 | 1 | 0x00 |  |
| 11 | Fossil Kit Control | 0 = Thermostat; 1 = External | 2 | 1 | 0 | 1 | 0x00 |  |
| 12 | Auto Changeover | 0 = Off; 1 = On | 2 | 1 | 0 | 1 | 0x01 | Yes |
| 13 | Auto Differential | 0 to 5 deg F | 0 | 1 | 0 | 5 | 0x03 | Yes |
| 14 | High Cool Stage Finish | 0 = No; 1 = Yes | 2 | 1 | 0 | 1 | 0x00 | Yes |
| 15 | High Heat Stage Finish | 0 = No; 1 = Yes | 2 | 1 | 0 | 1 | 0x00 | Yes |
| 16 | Aux Heat Droop | 0 = Comfort; 2 to 15 deg F from setpoint | 0 | 1 | 0 | 15 | 0x00 |  |
| 17 | Up Stage Timer Aux Heat | 0 = Off; 1 = 30 minutes; 2 = 45; 3 = 60; 4 = 75; 5 = 90 minutes; 6 = 2 hours; 7 = 3; 8 = 4; 9 = 5; 10 = 6; 11 = 8; 12 = 10; 13 = 12; 14 = 14; 15 = 16 hours | 2 | 1 | 0 | 15 | 0x00 |  |
| 18 | Balance Point (Compressor Lockout) | 0 = Off; 5 to 60 degrees F (in 5 degrees increments) | 0 | 1 | 0 | 60 | 0x00 |  |
| 19 | Aux Heat Lock Out (Aux Heat Outdoor Lockout) | 0 = Off; 5 to 65 degrees F (in 5 degrees increments) | 0 | 1 | 0 | 65 | 0x00 |  |
| 2 | Temp Scale | 0 = Fahrenheit; 1 = Celsius | 2 | 1 | 0 | 1 | 0x00 |  |
| 20 | Cool 1 CPH (Cooling cycle rate stage 1) | 1 to 6 CPH | 0 | 1 | 1 | 6 | 0x03 |  |
| 21 | Cool 2 CPH (Cooling cycle rate stage 2) | 1 to 6 CPH | 0 | 1 | 1 | 6 | 0x03 |  |
| 22 | Heat 1 CPH (Heating cycle rate stage 1) | 1 to 12 CPH | 0 | 1 | 1 | 12 | 0x03 |  |
| 23 | Heat 2 CPH (Heating cycle rate stage 2) | 1 to 12 CPH | 0 | 1 | 1 | 12 | 0x03 |  |
| 24 | Aux Heat CPH (Heating cycle rate Auxiliary Heat) | 1 to 12 CPH | 0 | 1 | 1 | 12 | 0x09 |  |
| 25 | EM Heat CPH (Heating cycle rate Emergency Heat) | 1 to 12 CPH | 0 | 1 | 1 | 12 | 0x09 |  |
| 26 | Compressor Protection | 0 = Off; 1 to 5 minutes | 0 | 1 | 0 | 5 | 0x05 | Yes |
| 27 | Adaptive Recovery | 0 = Off; 1 = On | 2 | 1 | 0 | 1 | 0x01 |  |
| 28 | Min Cool Temperature | 50 to 99 degrees F | 0 | 1 | 50 | 99 | 0x32 | Yes |
| 29 | Max Heat Temperature | 40 to 90 degrees F | 0 | 1 | 40 | 90 | 0x5A | Yes |
| 3 | Outdoor Temp | 0 = No; 1 = Wired | 2 | 1 | 0 | 1 | 0x00 |  |
| 30 | Air Filters | 0, 1 or 2 Filters | 0 | 1 | 0 | 2 | 0x00 | Yes |
| 31 | Air Filter 1 Reminder | 0 = Off; 1 = 10 Run Time Days; 2 = 20; 3 = 30; 4 = 45; 5 = 60; 6 = 90; 7 = 120; 8 = 150 Run Time Days; 9 = 30 Days; 10 = 45; 11 = 60; 12 = 75 Days; 13 = 3 Months; 14 = 4; 15 = 5; 16 = 6; 17 = 9; 18 = 12; 19 = 15 Months | 2 | 1 | 0 | 19 | 0x00 | Yes |
| 32 | Air Filter 2 Reminder | 0 = Off; 1 = 10 Run Time Days; 2 = 20; 3 = 30; 4 = 45; 5 = 60; 6 = 90; 7 = 120; 8 = 150 Run Time Days; 9 = 30 Days; 10 = 45; 11 = 60; 12 = 75 Days; 13 = 3 Months; 14 = 4; 15 = 5; 16 = 6; 17 = 9; 18 = 12; 19 = 15 Months | 2 | 1 | 0 | 19 | 0x00 | Yes |
| 33 | Hum Pad Reminder | 0 = Off; 1 = 6 Calendar Months; 2 = 12 Calendar Months | 2 | 1 | 0 | 2 | 0x00 | Yes |
| 34 | Dehum Filter Reminder | 0 = Off; 1 to 12 Calendar Months | 0 | 1 | 0 | 12 | 0x00 | Yes |
| 35 | Vent Filter Reminder | 0 = Off; 3, 6, 9, 12 Months | 0 | 1 | 0 | 12 | 0x00 | Yes |
| 36 | UV Devices | 0, 1 or 2 UV devices | 0 | 1 | 0 | 2 | 0x00 | Yes |
| 37 | UV Bulb 1 Reminder | 0 = Off; 6, 12, 24 Months | 0 | 1 | 0 | 24 | 0x00 | Yes |
| 38 | UV Bulb 2 Reminder | 0 = Off; 6, 12, 24 Months | 0 | 1 | 0 | 24 | 0x00 | Yes |
| 39 | Idle Brightness | 0 = Off; 1 to 5 Brightness level | 0 | 1 | 0 | 5 | 0x00 |  |
| 4 | Equipment Type | 0 = None; 1 = Standard Gas; 2 = High Efficiency Gas; 3 = Oil; 4 = Electric; 5 = Fan Coil, 6 = Air to Air Heat pump; 7 = Geothermal Heat Pump; 8 = Hot Water; 9 = Steam | 2 | 1 | 0 | 9 | 0x02 |  |
| 40 | Clock Format | 0 = 12 hour; 1 = 24 hour | 2 | 1 | 0 | 1 | 0x00 |  |
| 41 | Daylight Saving | 0 = Off; 1 = On | 2 | 1 | 0 | 1 | 0x01 |  |
| 42 | Temp Offset | 0 = Off; -3 to 3 degrees F (in 1 degree increments) | 0 | 1 | -3 | 3 | 0x00 | Yes |
| 5 | Reversing Valve | 0 = O/B on Cool; 1 = O/B on Heat | 2 | 1 | 0 | 1 | 0x00 |  |
| 6 | Cool Stages | 0, 1, 2 | 0 | 1 | 0 | 2 | 0x01 |  |
| 7 | Heat Stages; AUX/E stages | 0, 1, 2 | 0 | 1 | 0 | 2 | 0x01 |  |
| 8 | Aux/E Control | 0 = Both Aux/E; 1 = Either Aux/E | 2 | 1 | 0 | 1 | 0x00 |  |
| 9 | Aux Heat Type | 0 = Electric; 1 = Gas/Oil | 2 | 1 | 0 | 1 | 0x00 |  |
| 43 | Humidity Offset | 0 = Off; -12 to 12 percent (in 1 percent increments) | 0 | 1 | -12 | 12 | 0x00 | Yes |
| 44 | Z-Wave Temperature resolution | 0 = Advanced; 1 = Standard; 2, 3, 4, 5 | 0 | 1 | 0 | 5 | 0x01 | Yes |
| 45 | Z-Wave Humidity resolution | 1% to 5% | 0 | 1 | 1 | 5 | 0x01 | Yes |

Resideo Technologies, Inc.

Scottdale, AS

85254

www.resideo.com

© Resideo Technologies, Inc.